## Slide 1: Numerical on Zeolite Process

## Slide 2
A zeolite bed on softening of 40,000 litres of water gets exhausted, This zeolite bed requires 50 litres of 15% NaCl solution calculate hardness of water softened by zeolite bed.
Solution: Given, Volume of water made soft by zeolite = 40,000 lit.
Concentration of NaCl = 15 % = 150 g per lit.
Volume of NaCl required for regeneration = 50 lit.
To calculate Hardness of water = ?
Quantity of NaCl required for regeneration in mg = Conc. Of NaCl × Volume of NaCl × 1000
= 150 × 50 ×1000
= 7.5 × 106 mg
Numerical 1

## Slide 3
Quantity of NaCl in terms of CaCO3 equivalent = 7.5 × 106 × 50/ 58.5
= 6.4 × 106 mg CaCO3 equivalent
Hardness × litres of water = Quantity of NaCl in CaCO3 equivalent
Hardness × 40000= 6.4 × 106
Hardness = 6.4 × 106 /40000
Hardness = 160.25 mg/lit.
Numerical 1

## Slide 4
A zeolite bed on softening of 4500 litres of water having hardness 126 ppm gets exhausted, This zeolite bed is regenerated by NaCl solution having 10% concentration, how much litres of NaCl will be required for regeneration.
Solution: Given, Volume of water made soft by zeolite = 4500 lit.
Hardness of water = 126 ppm
Concentration of NaCl = 10% = 100 g per lit.
To calculate Volume of NaCl solution required for regeneration = Z Quantity of NaCl required for softening in mg = Conc. Of NaCl × Volume of NaCl × 1000
= 100 × Z ×1000
= Z × 105 mg of NaCl
Numerical 2

## Slide 5
Quantity of NaCl in terms of CaCO3 equivalent = Z × 105 × 50/ 58.5
= Z × 8.55 × 104 mg CaCO3 equivalent
Hardness × litres of water = Quantity of NaCl in CaCO3 equivalent
126 × 4500= Z × 8.55 × 104
Z = 126 × 4500/ 8.55 × 104
Z = 6.63 lit. of NaCl solution
Numerical 2

## Slide 6
A zeolite bed is regenerated by 10 litres of NaCl solution having concentration 10%, calculate how many litres of water having hardness 250 mg/lit. can be purified by the zeolite softener.
Solution: Given, Volume of NaCl solution required for regeneration = 10 lit.
Concentration of NaCl = 10% = 100 g per lit.
Hardness of water = 250 mg per lit.
To calculate Volume of water made soft by zeolite = Z lit.
Quantity of NaCl required for softening in mg = Conc. Of NaCl × Volume of NaCl × 1000
= 100 × 10 ×1000
= 1 × 106 mg of NaCl
Numerical 3

## Slide 7
Quantity of NaCl in terms of CaCO3 equivalent = 1 × 106 × 50/ 58.5
= 8.55× 105 mg CaCO3 equivalent
Hardness × litres of water = Quantity of NaCl in CaCO3 equivalent
250 × Z = 8.55 × 105
Z = 8.55 × 105/250
Z = 3418.8 lit. of Water
Numerical 3